## Slide 1: Analysis of Water Use and Consumption by Texas Power Plants
Gary Gibbs
Government & Environmental Affairs Manager, Texas
American Electric Power

## Slide 2: THE ISSUES
CONFUSION
RETRO-FIT
USE VS CONSUMPTION
WATER
ENERGY
COOLING
REPERCUSSIONS
?
Texas Center for Applied Technology
Texas Engineering Experiment Station
Texas A&M University System
Notes: There is confusion over the interdependence of energy and water and the influence of cooling technologies on that relationship
When this study was being initiated, it was being suggested that Texas power plants be retrofitted with the “latest” cooling technology without understanding the repercussions of such actions
There is a need to quantify water use and water consumption into an everyday context

## Slide 3: OBJECTIVES OF THE STUDY
CLARIFY
ECONOMIC IMPACTS OF MANDATING A SINGLE COOLING TECHNOLOGY
CONTEXT
ONCE-THROUGH
WET TOWERS
AIR COOLED CONDENSERS
+
=
USE
CONSUMPTION
Notes: The objectives of this study were to clarify the relationship between energy and water by accurately describing the different cooling technologies in terms of water consumption.
The term use is often substituted for the more specific terms withdrawal or diversion, which can confuse matters. Water use is a general term that can refer to either consumptive or non-consumptive use. Water use includes drinking, flushing toilets, irrigation, evaporative cooling, boating, fishing, and many other applications.
Water consumption refers to a water use that makes it no longer available for other uses. Examples are drinking water, evaporated water, or water incorporated into a product like corn or concrete. When water is consumed, it is no longer available in the system. Consumption is a truer, “big picture” measure of impact on water resources.
While performing an economic impacts analysis was outside the scope of this study, we did acknowledge the fact that there are economic impacts of mandating a single cooling technology whether Retrofitting or with a New build
The final, and possibly most significant objective was to present the results with proper context

## Slide 4: METHODS
ANALYZED MULTIPLE DATASETS TO QUANTIFY WATER USE-CONSUMPTION, & ENERGY USE-CONSUMPTION
REVIEW:
ARTICLES
REPORTS
WHITE PAPERS
SCHOLARLY WORKS
WEBSITES
DATABASES
COSTS
Notes: In order to clarify the relationship between energy and water and to describe the different cooling technologies in terms of water consumption, hundreds of articles, reports, white papers, peer reviewed scholarly works, websites, and online databases were reviewed.
The primary source of data for the costs of retrofits and new construction came from studies conducted by EPRI and Dr. John Maulbetsch.
Data for water use, water consumption, energy production, energy consumption, and demographics came from many sources including
  A sample from several power companies that participated in this study
  US Department of Energy
  US DOE, Energy Information Agency (EIA)
  US Geological Survey (USGS)
  USGS Circular 1344
The Texas Commission on Environmental Quality (TCEQ)
The Texas Water Development Board
The Office of the Texas Comptroller of Public Accounts
The Texas State Historic Society
  Used the most recent data (2010) possible in the study

## Slide 5: 2009 Water Consumption in Texas by Sector

## Slide 6
Condenser
“Once-Through” Reservoir Cooling System
Cooling Reservoir
Recirculated Cooling Water
As Needed
Makeup Water
Evaporation, Radiation, & Convection Cool Water
Generator
ELECTRICITY
Turbine
Process
Steam
Process Steam
from Boiler
Process Water
to Boiler
Warmed Water
Condenser
Cooled Water
Notes: With once-through systems cooling water is pumped through a condenser to condense the steam which is then pumped back to the boiler to complete the cycle. Virtually all the cooling water is returned to the cooling reservoir where it re-circulates, cools naturally, and can be pumped back to the condenser or used for other purposes (e.g. within the power plant, for recreation, or by other industrial users.)
Make up water can come from rain & storm water runoff and/or surface water. It may also use municipal wastewater treatment plant effluent.
It should be noted that the term “once-through” is appropriate where water is withdrawn and returned to a river, but can be misleading for cooling ponds where the same cooling water can be re-circulated through the system repeatedly.
Once-through cooling systems are the simplest, least expensive, and most effective technology for condensing steam, providing the best power plant efficiency (i.e. the most electricity is produced for the amount of fuel burned)

## Slide 7: EVAPORATIVE COOLING TOWER SYSTEM
Condenser
Turbine
Process
Steam
Recirculated Cooling Water
Generator
As Needed Makeup Water
Reuse in other Plant Processes
Treatment
Discharge
Blowdown
Evaporation Cools Water
ELECTRICITY
Process Water
to Boiler
Process Steam
from Boiler
Cooled Water
Warmed Water
Notes: Thermal power plants using wet cooling tower systems pump water from a water source through a condenser and then to a cooling tower. Large fans (forced draft) or hyperbolic designs (natural draft) provide air flow to dissipate the transferred heat from the cooling water to the air, primarily by means of evaporation. The cooled water is then re-circulated back to the condenser.
Make up water can come from rain & storm water runoff and/or surface water. It may also use municipal wastewater treatment plant effluent.
Wet cooling towers use less, but consume more water than once-through systems.

## Slide 8: TYPICAL DRY COOLING SYSTEM
Turbine
Fans
Air-Cooled
Condenser
Convection
Cools Steam
Process
Steam
Process Steam
from Boiler
Process Water
to Boiler
Generator
ELECTRICITY
Notes: With dry cooling, large fans (forced-draft) or hyperbolic towers (natural draft) generate air flow to condense the steam as it flows through finned tubes in the condensers. Cooling water is not needed because the steam is condensed as the heat is transferred directly to the air by means of convection.
The heat transfer to air via convection is less efficient than the previously described heat transfer mechanisms and the heat capacity of air is lower than water, so a significantly larger condenser, greater number and size of fans, and higher air flow are required than for traditional wet cooling towers.

## Slide 9: Electric Power Water Withdrawal and Population Trends

## Slide 10: Trend for Water Consumption per Unit Energy

## Slide 11: Water Use per Household in Texas
Typical American household = 4.6 people, 2,500 sf house, uses 29 kW of electricity each day
Typical Texas once-through plant consumes 9½ gallons of water to produce that 29 kW of power:
  5.7 gallons / day to power a home by NGCC w/OTC
In comparison, the typical American household consumes 300 gallons of water each day. Therefore only 3% of the total water consumed by the typical household is used to generate the electricity.

## Slide 12: RESULTS
MANDATING ONE TECHNOLOGY HAS CONSEQUENCES
  RETURN ON INVESTMENT
  PREMATURE RETIREMENT
  SUPPLY DEMAND
  RIPPLE EFFECT OF INCREASED COSTS
?
Notes:   Mandating one cooling technology could have significant consequences
    Limits investor’s ability to make a return on investment thereby discouraging future investment
    Cause premature retirement of multiple plants
    Hinder power producers’ ability to meet the electric demands of the citizens of Texas
    Cause a negative ripple effect on both the Texas economy and the national economy
  Water conservation is an integral part of current STANDARD OPERATING PROCEDURES for the Texas power industry. As a result :
    Texas once-through cooled power plants consume less than 10 gallons of water to produce the amount of electricity consumed per household per day
    Water consumption to energy production efficiency in Texas once-through cooled power plants has improved over time and continues to do so

## Slide 14: Conclusions
  Water consumption for utility industry typically less than 3% of state’s total consumption, and trend is decreasing
  The electric utility industry has dramatically reduced water consumption over the years, such that any further significant savings will require significant cost to electric customers.
  Only 3% of the electricity used daily in a typical household is required to withdraw, treat and deliver the water used -- and manage the resulting wastewater. Only 3%, what a bargain!!